## Slide 1
Leistungselektronik in der Aufbereitung, Übertragung, Verteilung und Speicherung elektrischer Energie
Power Electronics in Power Conditioning, Transmission Distribution and Storage of Electric Energy
Peter Zacharias
Universität Kassel, Kompetenzzentrum für Dezentrale Elektrische Energieversorgungstechnik (KDEE)
www.kdee.uni-kassel.de
Frühjahrssitzung des Arbeitskreises Energie der
Deutschen Physikalischen Gesellschaft 2013, Bad Honnef

## Slide 2
Outline of the Presentation
General Situation of the Electric Power Supply System with Germany as Example
New Types of Electric Generators with Power Electronic Converters (Solar, Wind Power)
System Problems and Power Electronic Solutions
Useful Life Time and Reliability
New Semiconductor Devices
Conclusions

## Slide 3
coal
nuclear
hydro
high
voltage
grid
medium
voltage
grid
Up to 10 years before
Central generation
Sizing for coverage of max. load
Time-invariant tariffs
Load rejection at customer
No information of grid status for customers
Strict power limits for feed-in
Large power reserves for unexpected
loads or failure of power plants required
Only unidirectional control required
low
voltage
grid
Ref: Prof. Dr. J. Schmid. ISET Kassel
1. General Situation of the Electric Power Supply System

## Slide 4: 1. General Situation of the Electric Power Supply System
Today and in future
Additional decentralised generation
Load coverage by trading
Time-variable tariffs
Load and cost optimisation by means of dialog
Power reserves will be reduced
by means of trade
Bidirectional communication and large flow of information
Up to date information by
means of variable tariffs
Variable power limitation depending on present load
wind farm
BZ
PV
Wind
BZ
PV
KWK
coal
nuclear
hydro
gas and steam
Ref: Prof. Dr. J. Schmid. ISET Kassel

## Slide 5
Hydro
Wind
Bio Mass
Solar
1. General Situation of the Electric Power Supply System: New Types of Generators

## Slide 6: 1. General Situation of the Electric Power Supply System: Implementation of Converters for Wind and Solar Energy
(source: BMU 2012, e.on)
Total power of active German utility companies: 85-95GW
Total installed power: ~118GW

## Slide 7
New Types of Electric Generators: Solar Energy Converters
Source: SMA Solar Techology AG, Niestetal: 38MWp Solar Park Waldpolenz

## Slide 8
Activ Solar's 100 MW Perovo PV plant
in Ukraine's sunny Crimean Peninsula,
commissioned in December 2011
Large installations are coming up quickly due to decreasing investment costs and predictable maintanence costs compared to solar thermal installations
System size: higher and higher power
Source: List of photovoltaic power stations. Wikipedia 2012
New Types of Electric Generators: Solar Energy Converters

## Slide 9
New Types of Electric Generators: Conversion Tasks
3~ IGBT inverter principle

## Slide 10
Growth of wind energy converters since the beginning of electric power production [source: ISET, Kassel]
New Types of Electric Generators: Wind Energy Converters

## Slide 11
source: http://www.spiegel.de
New Types of Electric Generators: Wind Energy Converters

## Slide 12
induction generator in it‘s simplest configuration: squirril cage induction generator
Small power only
No FRT control
induction generator with squirril cage induction generator + back to back converter
Up to 2MW
Big size
Full FRT Control
P
grid
New Types of Electric Generators: Wind Energy Converters

## Slide 13
Doubly Fed Induction Generator (DFIG)
Only 1/3 of Power to be handled by electronic power converter
FRT Problems
Synchronous Generator (SG)
Full power to be handled by electronic power converter
Full FRT control
New Types of Electric Generators: Wind Energy Converters

## Slide 14
DC link voltage 1100V
AC output 3~690V
Phase current 837A
IGBT current density ~1A/mm2 @1700V class
Diode current density ~2A/mm2 @1700V class
active Silicon area 150cm2/MVA
Full 5MVA back to back converter requires >750cm2 Silicon!
Only 1/3 of total power to be handled by electronic power converters for doubly fed induction generators
New Types of Electric Generators: Wind Energy Converters

## Slide 15
2. New Types of Electric Generators: Basic Conversion Tasks

## Slide 16: Market situation developments of PV solar power
(source: European Photovoltaic Industry Association (EPIA), 2015 – Global Market Outlook for Photovoltaics until 2015)
Market Scenario for new PV Installations worldwide until 2015
10GW = 25.000M€ investment !
2. New Types of Electric Generators: Market Opportunities

## Slide 17
3. System Problems and Power Electronic Solutions: Transmission
Transmission grid can be completed with a HVDC overlay grid (source: VDE)

## Slide 18
Transmission needs within Germany
DC AC
under construction or planned
Example:
Local situation
at Kassel
3. System Problems and Power Electronic Solutions: Transmission

## Slide 19
HVDC: New Applications in Europe
a) planned offshore wind parks in the North Sea [Valov, Zacharias, ISET],
b) already existing sea cables for interconnecting grids in Europe [source: ABB],
c) proposed inter-continental grid extension for RE sources in North Africa and Europe
[source: DESERTEC Foundation]
3. System Problems and Power Electronic Solutions: Transmission

## Slide 20
3. System Problems and Power Electronic Solutions: Transmission
active Silicon area >15m2/GW !
Principle of HVDC Transmission System with
Voltage Source Performance and Capability for Grid Control

## Slide 21
Wind
Solar
Total
MWh/h
Feed-in Wind and Solar Power in Germany accumulated in March-May 2011 (Source: TSO‘s; ÜNB)
3. System Problems and Power Electronic Solutions:
Transmission Fluctuations

## Slide 22
Data: ENTSO-E, Diagram: BNetzA
MWh/h
Total German Energy Trading 2011
 Quicker change of power flow directions!
3. System Problems and Power Electronic Solutions:
Transmission Fluctuations

## Slide 23: Feed in Solar & Wind Power in Comparison to Energy Export (+) and Import (-) in Spring 2011
Data: Entso-E, EEX
Diagram: BNetzA
Switch off of
nuclear power
Wind power [MWh/h]
Solar power [MWh/h]
German power excess [MWh/h]
 Quick Change of Power Flow

## Slide 24
Solution Approaches:
Generation and Load Profile Prognosis
Demand Side Management*
Long Distance Energy Trade within Europe  Power Flow Control*
Energy Storage Implementation*
* Power Electronics is helpfull or necessary!
3. System Problems and Power Electronic Solutions:
Transmission Fluctuations

## Slide 25
Week of the maximum PV energy yield /Germany
Day of the week
Power production & consumption [GW]
(Study:Rolle der Solarstromerzeugung in zukünftigen Energieversorgungsstrukturen - Welche Wertigkeit hat Solarstrom?, requested by Federal Ministery BMU, May 2008, ISET e. V. Kassel, BMU 2012
Peak power shedding…No limits?
conv. power
in 2011
Wind 29,1GW
PV 24,8GW (BMU 2012)
3. System Problems and Power Electronic Solutions:
Transmission Fluctuations

## Slide 26
Peak power shedding… No limits?
In principle : Yes!...
But we have already realized now the 50,2Hz problem:
PV solar low power systems switch immediatly off, if 50,2Hz is exceeded!
(This is due to regulations established, when PV power did not play any role in the grid)
What does this mean?
3. System Problems and Power Electronic Solutions:
Basic Problem: Voltage and Frequency Control of the Grid

## Slide 27
Solar PV power achieved a significant share of the installed power in the
German power system (total 118GW), but small sized systems (the majority)
disconnect from the grid automatically, if the grid frequency exceeds 50,2Hz
(source: BMU 2012, e.on)
3. System Problems and Power Electronic Solutions:
Basic Problem: Voltage and Frequency Control of the Grid

## Slide 28
(110/20kV near Braunschweig)
ΔP=1GW  Δf≈0,08Hz
The Italian blackout in 2003 would have caused a European blackout at today conditions!
(But this has been occurred in the dark morning)
50,2Hz limit of PV inverters
(souce: S. Heier, University of Kassel)
3. System Problems and Power Electronic Solutions:
Basic Problem: Voltage and Frequency Control of the Grid

## Slide 29
Consequences for all smaller systems:
Significant amount of PV systems must be refurbished by changing the switch off limits statistically in a wide band or continuous power reduction if frequency exceeds a certain limit
Future systems have to take part in grid frequency control
 More complex systems already at lower power level!
 Larger power (PV) installations have to follow the grid code for MV and HV systems already since 2001!
3. System Problems and Power Electronic Solutions:
Basic Problem: Voltage and Frequency Control of the Grid

## Slide 30
The renewable sources need backup sources indeed, but destroy (supported by law) the business cases of the existing fast reacting power plants like pumped storage power station or gas power plants
An increase to up to 200GWp of renewable sources (as being discussed at the moment) will destroy even the business cases of base (coal) power stations.
Load shifting opportunities exist but are overestimated by far.
Long distance transmission may discharge the problem.
 These problems cannot be solved by power electronic solutions, but only by (European – wide) market regulations!
3. System Problems and Power Electronic Solutions:
Transmission Fluctuations

## Slide 31
voltage, %
frequency, Hz
47,5 49 50,25 51,5
87,5
110
115
continuous operation
< 30 minutes
 at frequency < 47,5 Hz or > 51,5 Hz: undelayed trip
load shedding
reduction of delivered power
Introduction into basics of grid control: voltage and frequency control
3. System Problems and Power Electronic Solutions:
Basic Problem: Voltage and Frequency Control of the Grid

## Slide 32
Frequency droop
Voltage droop
Power plants are controlled by droops:
> With frequency droop parameters
of each generator can be con-
trolled their share of active power
globally within the grid!
> Grid voltage can be controlled locally at the interconnection point by injection of reactive power
3. System Problems and Power Electronic Solutions:
Basic Problem: Voltage and Frequency Control of the Grid

## Slide 33: What is the problem about?  Grid Voltage Control in Low and Medium Voltage Grids
source: B. Engel/ SMA Solar Technology
PV
P
P
P
20
kV
Trafo
0
,
4
kV
line
HAS1
HAS2
load1
load
2
PV
P
3
~
~
transformer station
Q
Q
U
length
1
,
1
p
.
u
. =
253
V
1
,
0
p
.
u
. =
230
V
high solar power
at low load
max. load (with voltage adjustment)
0
,
9
p
.
u
. =
207
V
additional injection of
reactive power
3. System Problems and Power Electronic Solutions:
Basic Problem: Voltage and Frequency Control of the Grid

## Slide 34
New control demands to low voltage distribution grids due to high density of distributed power generation
Important criteria: voltage tolerance according to DIN EN 50160 (230V +/-10%)
Voltage criteria is much more limiting the PV power to be connected to the low voltage grid than the line cross section for the current
Further explanations of the problem:
3. System Problems and Power Electronic Solutions:
Basic Problem: Voltage and Frequency Control of the Grid

## Slide 35
J. P. da Costa et. al.: Uni Kassel, KDEE, 2011
3. System Problems and Power Electronic Solutions:
Basic Problem: Voltage and Frequency Control of the Grid

## Slide 36
J- P- da Costa, Uni Kassel, KDEE
J. P. da Costa et. al.: Uni Kassel, KDEE, 2011
3. System Problems and Power Electronic Solutions

## Slide 37
J- P- da Costa, Uni Kassel, KDEE
J. P. da Costa et. al.: Uni Kassel, KDEE, 2011
3. System Problems and Power Electronic Solutions

## Slide 38
J- P- da Costa, Uni Kassel, KDEE
J. P. da Costa et. al.: Uni Kassel, KDEE, 2011
3. System Problems and Power Electronic Solutions

## Slide 39
J- P- da Costa, Uni Kassel, KDEE
J. P. da Costa et. al.: Uni Kassel, KDEE, 2011
3. System Problems and Power Electronic Solutions

## Slide 40
J- P- da Costa, Uni Kassel, KDEE
J. P. da Costa et. al.: Uni Kassel, KDEE, 2011
3. System Problems and Power Electronic Solutions

## Slide 41
Power electroncis based voltage control in distribution grids
opens a new huge market for power electronics
Intelligent unified power controlling substation (UPFC) in the LV grid
Increasing the hosting capacity of LV grids up to 200% with power electronics!
cable length [m]
Q, P
3~400V
W. Kruschel, J.P. da Costa, P. Zacharias, D. Mende, T. Bülo.
Case Study: Use of Power Electronic Voltage Regulators in Low
Voltage Distribution Networks.. ECPE Workshop, Kassel, März 2013

## Slide 42
Medium voltage distribution systems are influenced from higher voltage side (especially wind and excess of solar power) and have limited possibilities for reaction  medium voltage control becomes important
Source: diploma theses J. Busold; Uni Kassel 2012
Measurements at a 110kV/20kV transformer at 26th May 2012 near Kassel
3. System Problems and Power Electronic Solutions

## Slide 43: General Problems in recent Electricity Networks
Visualisation of the voltage distribution in a medium voltage grid (green: close to the nominal voltage, red: close to the upper limit)
Source: master thesis J. Busold , Uni Kassel 2012
Feed in of distributed power sources

## Slide 44: 4. Useful Life Time and Reliability: Maximum Power Cycles of Bonds at IGBT Standard Modules
Primary data: Application Notes eupec 2004
Number of cycles

## Slide 45: 4. Useful Life Time and Reliability: Cosmic Particle Flow
Cosmic particle interaction in compa-rison to the Mont Blanc mountain, according to an idea of CERN
Sources: J. F. Ziegler, “Terrestrial cosmic rays intensities,” IBM Journal of R & D,
Vol. 42, No. 1, pp. 117-140, 1998;
A. Astbury and D. Axen: Comparison of GEANT4 Simulation of Atmospheric Cosmic Rays with Measured Terrestrial Muon and Neutron Spectra, TRI--PP--06--14, Nov 2006

## Slide 46: FIT rates caused by cosmic rays at semiconductors at sea level (pn-Dioden, Schottky-Dioden, IGBTs; 600V...6500V)
Chart: nomalized DC voltage Ud/Unom
| 0.53030303030303028 | 0.54545454545454541 | 0.60606060606060608 | 0.72727272727272729 | 0.66666666666666663 | 0.75757575757575757 | 0.90909090909090906 | 0.96969696969696972 | 0.56923076923076921 | 0.61538461538461542 | 0.69230769230769229 | 0.76923076923076927 | 0.57999999999999996 | 0.6 | 0.64 | 0.8 | 0.9 | 0.61363636363636365 | 0.68181818181818177 | 0.72727272727272729 | 0.81818181818181823 | 0.90909090909090906 | 0.6 | 0.75 | 0.85 | 0.6 | 0.75 | 0.92 | 0.56785714285714284 | 0.59571428571428575 | 0.63771428571428568 | 0.67500000000000004 | 0.76500000000000001 | 0.88057142857142856 | 0.5312260531286912 | 0.55300023889221128 | 0.5879011655673253 | 0.63661473496993193 | 0.69623539116252153 | 0.76272545507471667 | 0.60448823258559448 | 0.63842833253636022 | 0.68752740586124605 | 0.71338526503006816 | 0.83376460883747849 | 0.99841740206814045 | 0.67500000000000004 | 0.7 | 0.73750000000000004 | 0.83333333333333337 | 0.91666666666666663 | 1 | 0.75 | 0.83333333333333337 | 0.91666666666666663 | 1 | 0.95833333333333337 | 1
 | 0.12959 | 0.99681 | 100.6783 | 2990.4448
 | 0.99681 | 29.9044 | 996.8149 | 2990.4448
 | 0.99681 | 9.9681 | 179.4267 | 1096.4964
 | 0.01 | 0.15 | 6 | 3000 | 80000
 | 18 | 300 | 1300 | 7000 | 15000
 | 6 | 4000 | 100000
 | 0.1 | 200 | 100000
 | 0.1 | 1 | 10 | 100 | 1000 | 10000
 | 0.1 | 1 | 10 | 100 | 1000 | 10000
 | 0.1 | 1 | 10 | 40 | 1000 | 10000
 | 214.2857 | 428.5714 | 1178.5714
 | 3571.4286 | 14285.7143 | 42857.1429
Sources of basic data: ABB Semiconductors, Infineon AG, Microsemi,
Soelkner, G. et al. in Materials Science Forum Vols. 556-557, (2007)
4. Useful Life Time and Reliability: Cosmic Particle Flow

## Slide 47
Assuming the same
FIT rates for
Si and SiC
at 1200V class
Ud
Ud
Influence of lower chip area on fail rate
0%
10%
20%
30%
40%
50%
60%
70%
80%
90%
100%
0
100
200
300
400
500
600
700
800
900
1000
1100
1200
DC link voltage U
d
[V]
likelyhood to fail within 20 years
Silicon
IGBT
3Gen
active area :
4,5cm
2
Silicon Carbide
VJFET
3Gen
active area :
0,6cm
2
4. Useful Life Time and Reliability: Cosmic Particle Flow

## Slide 48
Summary on the cosmic particle flow
Shielding of cosmic rays is realistically not possible
Malfunction is technology dependent (internal field strength profile)
Related to chip area, may calculated if failure rates are known
Si und SiC seem to perform comparably
Higher altitude of application or systems closer to the earth poles increase the problem
Rule: for longlife installations: Ud < 2/3 Unom!
4. Useful Life Time and Reliability: Cosmic Particle Flow

## Slide 49: 5. New Semiconductor Devices
At research level :
In the Market:
Sunny Tripower 20kW
Dez. 2011
99%
98%
ISET/University of Kassel
March 2008
98,8%
Fraunhofer ISE
July 2009
99,03%
KTH
Dez. 2011
99,7%
(Filter / devices in parallel?)
92%
101% ?

## Slide 50: 5. New Semiconductor Devices: Wide Band Gap Devices
Source: S. Araújo: Wide Band-Gap Power Devices in Power Conversion for Renewables, ECPE Workshop „Power Electronics in the Electrical Network”, 12 – 13 March 2013, University of Kassel

## Slide 51: 5. New Semiconductor Devices: Wide Band Gap Devices
Source: S. Araújo: Wide Band-Gap Power Devices in Power Conversion for Renewables, ECPE Workshop „Power Electronics in the Electrical Network”, 12 – 13 March 2013, University of Kassel

## Slide 52: 5. New Semiconductor Devices: Wide Band Gap Devices
Source: S. Araújo: Wide Band-Gap Power Devices in Power Conversion for Renewables, ECPE Workshop „Power Electronics in the Electrical Network”, 12 – 13 March 2013, University of Kassel

## Slide 53: 5. New Semiconductor Devices: Wide Band Gap Devices
Source: S. Araújo, PhD thesis, University of Kassel 2013

## Slide 54: 5. New Semiconductor Devices: Size reduction with SiC switches
First measurements indicate peak efficiency around 99% at 48kHz without overrating of semiconductor devices
Further increase of switching frequency to be investigated
Possible increase of power level (board already constructed for 11kW with possible parallel connection of two JFETs)
Araújo, S./ Uni-Kassel / Presented at PCIM Nuremberg 2011

## Slide 55: 5. New Semiconductor Devices: Japanese Programs for SiC
Fuji Electric,
TIA Power Electronic Summer School, Tsukuba 2012

## Slide 56: 6. Zusammenfassung
Durch die Umgestaltung des Energieversorgungssystems spielt die Leistungselektronik eine immer größere Rolle in allen Systembereichen
Mit leistungselektronischen Konvertern hat man flexible Systemkomponenten zur Bereitstellung der elektrischen Energie, der flexiblen Steuerung der Energieströme und der Qualität des elektrischen Energie beim Verbraucher
Die hohen Lebensdauererwartungen von 20-50 Jahren stellen an die Halbleiterbauelemente hohe Erwartungen, die durch neue Halbleiter mit hohem Bandabstand erfüllt werden können

## Slide 57
Thank you for your attention!
Vielen Dank für Ihre Aufmerksamkeit!
Please visit us at:
Besuchen Sie uns auf: www.kdee.uni-kassel.de