## Slide 1: "Entwicklungsstand und Perspektiven der solarthermischer Kraftwerke Robert Pitz-Paal Deutsches Zentrum für Luft- und Raumfahrt Institut für Solarforschung Inhalt Märkte Spanien USA RoW Kosten Kostensenkung Wert von Strom
1

## Slide 2
Konventionelle Kraftwerke
Was ist CSP?
2

## Slide 3
Solarthermische Kraftwerke
Was ist CSP?
3

## Slide 4: Warum Wärmespeicher?
2000 h
2000 h
>95%
 = 75%
200 h
deckt Lasten zuverlässig
4

## Slide 5: CSP F&E Strategie: hohe Konzentration + hohe Temperatur = hohe Effizienz => geringe Kosten
(Tabsorber =Tprocess) [K]
max
csp= th,Carnot* absorber
Parabolic Trough
C =100
Solar Tower
C=1000
5

## Slide 6: Der Markt in Spanien Aufbruch….und Niedergang
6

## Slide 7
Update on the situation of STE in Spain
  50 STE plants (2302,9 MWe) are finally in operation. No STE plant is currently under construction or promotion
45 PT plants (2222,5 MWe):
- Parabolic trough technology:
Eighteen 50MWe-plants with 1GWht TES
One 22.5MWe-plant hybridized with biomass
Twenty six 50MWe-plants without TES
3 CR plants (49,9 MWe)
Two saturated steam receiver plants
(10MWe and 20MWe)
One molten salt receiver plant (19MWe
- Central receiver technology:
2 LF plants (31,4 MWe), with saturated
steam and no TES
- Compact Linear Fresnel technology:
7

## Slide 8
Update on the situation of STE in Spain
  Two weeks ago the Spanish Government has issued for comments the calculation procedure to determine the committed Complementary Payment . The Spanish STE sector does not accept this proposal because the profitability would not be 7,5% but 4% only.
  In June 2013, a new law issued by the Spanish Government removed the feed-in tariff and all RE power plants must go to the Pool and they will be paid according to the pool price, plus a Complementary Payment to assure a “reasonable profitability” for investors (7.5%). The procedure to determine the amount of the complementary payment is not yet legally implemented
  In the period January 2012 – February 2013 the legal framework for STE plants in Spain was drastically modified by the Government, thus reducing the incomes of the plants by 37%
  50 STE plants (2302,9 MWe) are finally in operation. No STE plant is currently under construction or promotion
8

## Slide 9: Projects in Spain – Parabolic Troughs
Slide Source: C. Montoya, IDAE
IBERSOL PUERTOLLANO | 
Town | Puertollano
Province | Ciudad Real
Capacity (MW) | 50
Technology | Parabolic Trough
Storage | No
Plant Surface | 175 Ha
Components | Mirrors FLABEG & RIOGLASS Structure EUROTHROUGH Pipes SOLEL y SCHOTT Turbine SIEMENS
Startup | 2009
PROMOTER | IBERDROLA (90%), IDAE (10%)
9

## Slide 10: Gemasolar Tower plant, 15 h storage 19.9 MW (Torresol Energy)
10

## Slide 11
Macroeconomic Impact of the Solar Thermal Electric Sector in Spain
Download: www.estelasolar.eu
www.protermosolar.com
Available in English and Spanish
Slide courtesy of: Luis Crespo, Estela, Spain
11

## Slide 12
Premiums: 185 M€
Savings in CO2 rights: 5 M€
Savings from replacing imported fossil fuels: 24 M€
Fiscal contribution (S.S. Corporate and personal Taxes : 407 M€
Premiums: 185 M€
Support policy for STE …
Contribution to GDP: 1650 M€
+ Avoiding subsidies for 24000 employees
+ Leadership of the Spanish industry
+ Reducing hourly pool prices
+ Regional economical convergence
+ Local taxes
… an efficient economic and technological decision for Spain
2010 Figures
Note:
At the end of 2010 500 MW were in operation. Most of them were connected during the second half of the year. That is why savings in fuel and CO2 were so low. In 2012 these savings will be greater than 300 M€ and 50 M€ respectively.
Slide courtesy of: Luis Crespo, Estela, Spain
12

## Slide 13
STE jobs in Spain
Slide courtesy of: Luis Crespo, Estela, Spain
13

## Slide 14
Technology Development
Component manufacturing
Basic Engineering
Site Development
Project development
EPC
Detailed engineering
Construction
Operation and Maintenance
TOTAL LOCAL CONTENT 50% 80%
Past situation
Current Capabilities
Spanish
Foreign
Localization: A very fruitful period in Spain
From the first large plants connected in 2008 till the new ones
Slide courtesy of: Luis Crespo, Estela, Spain
14

## Slide 15: US Market: Bigger is better…..
15

## Slide 16: USA CSP Market Status
Currently Operating
  SEGS 1-2 (Cogentrix) 44 MW
  SEGS 3-9 (FPL/NextEra) 310 MW
  Nevada Solar One (Acciona) 64 MW
  Martin (FPL/NextEra) 75 MW
  Coalinga (BrightSource) 10 MW
  Sierra (eSolar) 5 MW
  Kimberlina (Areva) 5 MW
  Holaniku (Sopogy) 2 MW
  Maricopa (SES) 2 MW
  Saguaro (APS) 1 MW
  Cameo (Abengoa) 1 MW
  Ivanpah (BrightSource) 392 MW $1.6B LG (Tower)
  Solana (Abengoa) 280 MW w/ storage $1.4B LG (Trough)
Under construction
  Crescent Dunes (SolarReserve) 110 MW w/ storage $0.7B LG (Tower)
  Genesis (FPL/NextEra) 250 MW $0.8B LG (Trough)
  Mojave (Abengoa) 250 MW $1.2B LG (Trough)
  TOTAL 1,801 MW $5.7B LG (Loan Gurantee)
16
Nevada Solar One, Las Vegas, NV
Sierra Project, Lancaster, CA

## Slide 17: 280 MW plant Solana (Abengoa) now in operation (10. Oct 2013)
280 MW, 6 hours storage (molten salt), Solar field 2.2 M m2, Area 1200 ha, 980 GWh annual energy production.
17
Notes: Currently largest solar plant in operation.

## Slide 18: Ivanpah (Brightsource) solar tower 130 MW connected to grid, September 24, 2013 (Total 390 MW)
18

## Slide 19: Cresent Dunes (100 MW Molten Salt, 6 h Storage)
19

## Slide 20: Project Status October 2013
http://www.nrel.gov/csp/solarpaces/
20

## Slide 21: Technology Status October 2013
http://www.nrel.gov/csp/solarpaces/
21

## Slide 22: CSP Marktwachstum
Das projizierte Wachstum der CSP Stromerzeugung ist weiterhin sehr stark, mit einer gewissen Verlangsamung in 2014-2016 gegenüber früheren Vorhersagen
Quelle: IEA, MTRMR 2013
Projektion der CSP Stromerzeugung (TWh)
Top 10 Länder für kumulierte installierte CSP Kapazität in 2020 (MW)
Quelle: Bloomberg New Energy Finance

## Slide 23: Regionale Treiber und Befähiger
FIT (Feed in Tariff)
Governmental Loan
Guaranties
ODA (Official Development Assistance)
Individually guaranteed PPAs
Environmental awareness / climate change
Portfolio standards,
Directives (EU)
Export of REN
Opportunity costs from subsidized Oil/Gas
Demand match in Grids with high REN share
Independence from Energy
Import / growth with REN
Treiber
Befähiger
Die Treiber und Befähiger für CSP Technologie sind unterschiedlich für jede Region

## Slide 24: CSP in China
China has 5 solar thermal power systems in operation
China has about 25 sets of solar thermal collecting experiment facilities,
14 companies that can produce parabolic trough receiver tube
4 companies that can mass produce trough glass reflector mirror,
2 companies can provide the EPC for tower type collector systems,
2 companies can produce turbine for CSP.
24

## Slide 25: Stromgestehungskosten
25

## Slide 26: Current levelised cost of electricity from CSP ranges from $140/MWh to $360/MWh, depending on location, technology, thermal storage size & competition
Note LCOE for Levelised Cost of Electrlicity
Source: SBC Energy Institute Analysis based on IRENA (2012), “Renewable Energy Technologies: cost analysis series. Concentrating Solar Power”, NREL SolarPaces database (http://www.nrel.gov/csp/solarpaces/by_project.cfm) and BNEF
Economics, financing & key players – Levelised Cost of Electricity
ESTIMATED LCOE FOR EXISTING AND PROPOSED CSP PLANTS
USD2010 / kWh
Current levelised cost of electricity from CSP varies widely depending on project, concentrator technology and solar resource:
  Solar tower LCOE is estimated to range from 140 $/MWh and 270 $/MWh
  Parabolic trough LCOE is estimated to range from 150 $/MWh and 300 $/MWh
The cost is highly dependent on the available sunlight and on storage, which dictate the capacity factor
Datang
50 MW - China
Ouarzazate
160 MW - Moroco
2,635 kWh/m2/y
Godawari
50 MW India
Solnova 1 - 3
50 MW each - Spain
2,012 kWh/m2/y
Extresol 1 & 2
50 MW each - Spain
2,168 kWh/m2/y
Andasol 1- 3
50 MW each - Spain
2,136 kWh/m2/y
SEGS II – VIII
30 MW each -US
2700 kWh/m²/y
IEA SSPS
500 kW
(2000 kWh/m²/y
SEGS I
13.8 MW - US
2700 kWh/m²/y
SEGS VIII & IX
89 MW each - US,
2700 kWh/m²/y
0.7
0.6
0.5
0.4
0
0.1
0.2
0.3
2005
2010
2015
2000
1995
1990
1985
1980
Dhursar
100 MW - India
2062 kWh/m2/y
Puerto Errado 2
30 MW – Spain
2,095 kWh/m2/y
Tonopah
110 MW – US
2,685 kWh/m2/y
PS20
20 MW - Spain
2,012 kWh/m2/y
Gemasolar
20 MW - Spain
2,172 kWh/m2/y
PS10
11 MW - Spain
2,012 kWh/m2/y
Supcon
50 MW -China
LFR
Tower
Trough
Name
Project Capacity – Country
Direct Normal Irradiance

## Slide 27: Der Wert von Elektrizität…. Beispiel Kalifornien 32% Renewable Portfolio Standard
27

## Slide 28
P. Denholm,
The Value of CSP with Thermal Energy Storage
SolarPACES 2013
28

## Slide 29
5,6-6,3 $/MBtU
36 $/t
29

## Slide 30
30

## Slide 31: Dispatch Strategien
Sommer
Winter
31

## Slide 32
32

## Slide 33
P. Denholm,
The Value of CSP with Thermal Energy Storage
SolarPACES 2013
33

## Slide 34: Ansätze zur Kostensenkung
34

## Slide 35: Einfluss der oberen Prozesstemperatur Beispiel Parabolrinnenkraftwerk: Thermoöl 394°C
htherm 40.3%
383°C
103 bar
394°C

## Slide 36: Einfluss der oberen Prozesstemperatur Beispiel Parabolrinnenkraftwerk: Salzschmelze 545°C
htherm 43.5%
545°C
525°C 120 bar

## Slide 37: Einfluss der oberen Prozesstemperatur Größenvergleich Solarfeld
195 ha
1500 m
1300 m
bei Salz- statt Ölsystem Einsparung an Kollektorfläche
~ 7-10% (bei gleichem Jahresertrag
an einem guten Standort)

## Slide 38: Einfluss der oberen Prozesstemperatur HS-Diagramm des Wasser-Dampf-Kreislaufs für Öl- und Salzsystem

## Slide 39: Einfluss der oberen Prozesstemperatur Einbußen an der Niederdruckentspannung durch Trockenkühlung
Dh = 951 kJ/kg
Dh = 1175 kJ/kg
Dh=83 kJ/kg
~ 8.7% für Öl
~ 7.0 % für Salz
Einfluß der Trockenkühlung
auf thermischen Wirkungsgrad
des Gesamtsystems:
Öl: - 5.3%
Salz: - 4.4 %
Nasskühlung pkond=47 mbar
Trockenkühlung pkond=100 mbar

## Slide 40: Einfluss der oberen Prozesstemperatur Größenvergleich Speichersystem
290 °C
550 °C
292 °C
386 °C
Salzsystem
Ölsystem
27500 t
10000 t
Speicherinventar für 7.5 h bei 50 MW
d=37 m
d=26 m
V=32%
V=17%
V=17%
V=5%
2,5%

## Slide 41: LCoE Results – Head to Head Race !
Chart: 
| Power Tower 100 MWe SSe | 50 MWe ET, VP-1 @ 393 °C | 50 MWe UT, VP-1 @ 393 °C | 100 MWe UT, VP-1 @ 393 °C | 100 MWe UT, SSe @ 550 °C | 200 MWe UT, SSe @ 550 °C | 200 MWe UT, HypoHitec @ 550 °C
Daggett | 10.8 | 16.9 | 15.4 | 13.9 | 11.2 | 10.2 | 9.9
Abu Dhabi | 11 | 17.6 | 16 | 14.4 | 11.5 | 10.6 | 10.3
LCoE in €/kWh
-9 %
-10 %
-20 %
-10 %
-3 %
-40 %
Weinrebe et al:
Molten Salt for Parabolic Trough Applications: System Simulation and Comparison with a Power Tower
SolarPACES 2013
Cost comparison Tower / Trough (Ultimate Trough) w/ Salt as HTF
41

## Slide 42
Strategy and Approach
Helmholtz funding for high risk / high reward approach:
  Tower systems using advanced salt mixtures, liquid metals or solid particles at T > 650°C with ηsys > 20%
  Reduce uncertainty by gaining scientific understanding of full system to convince industry to engage in scale-up
High Concentration + High Temperature = High Efficiency = Low Cost
Advanced heat transfer media needed for:
    high temperature operation
    efficient storage integration
  to break todays temperature limit of 550°C
C=100
C=1000
42
Notes: 42

## Slide 43: Key Scientific Questions and Topic Structure
43
Subtopic 1
Advanced Heat Transfer Media
Can molten salt mixtures, liquid metals or ceramic particles be used as efficient heat transfer media at T>650° to achieve ηsys > 20% ?
Subtopic 2
Impact of Desert Environment
Is the concept fit to be operated for > 20 years in a desert environment?

## Slide 44: Key Scientific Questions and Topic Structure
44
Understand the system!
Target 2019: Proof of concept in 100 - 500 kW scale as a basis for tech-transfer

## Slide 45: Subtopic 1 - Advanced Heat Transfer Media
Achievements in POF II
System models show high efficiency potential
results in lower LCOE
Can molten salt mixtures, liquid metals or ceramic particles be used as efficient heat transfer media at T > 650° to achieve ηsys > 20% ?
45
falling particle receiver, 800°C

## Slide 46: Subtopic 1 - Advanced Heat Transfer Media
Achievements in POF II
System models show high efficiency potential
Prototype of particle receiver prove feasibility in 10 kW scale up to 900°C
Particle receiver test at 900°C
Can molten salt mixtures, liquid metals or ceramic particles be used as efficient heat transfer media at T > 650° to achieve ηsys > 20% ?
46

## Slide 47: Subtopic 1 - Advanced Heat Transfer Media
Achievements in POF II
System models show high efficiency potential
Prototype of particle receiver prove feasibility in 10 kW scale up to 900°C
Suitable salt mixtures identified
Can molten salt mixtures, liquid metals or ceramic particles be used as efficient heat transfer media at T > 650° to achieve ηsys > 20% ?
47

## Slide 48: Subtopic 1 - Advanced Heat Transfer Media
Achievements in POF II
System models show high efficiency potential
Prototype of particle receiver prove feasibility in 10 kW scale up to 900°C
Suitable salt mixtures identified
Heat transfer correlations for channel/bundle flows with up to 500 kW in PbBi established
Can molten salt mixtures, liquid metals or ceramic particles be used as efficient heat transfer media at T > 650° to achieve ηsys > 20% ?
48

## Slide 49: Subtopic 1 - Advanced Heat Transfer Media
10 kW Receiver and auxiliaries design, built and tested for all fluids
Goals and milestones
Can molten salt mixtures, liquid metals or ceramic particles be used as efficient heat transfer media at T > 650° to achieve ηsys > 20% ?
49

## Slide 50: Subtopic 1 - Advanced Heat Transfer Media
10 kW Receiver and auxiliaries design, built and tested for all fluids
Evaluation of degradation effects on structural materials on all HTM
Goals and milestones
Can molten salt mixtures, liquid metals or ceramic particles be used as efficient heat transfer media at T > 650° to achieve ηsys > 20% ?
50

## Slide 51: Subtopic 1 - Advanced Heat Transfer Media
10 kW Receiver and auxiliaries design, built and tested for all fluids
Evaluation of degradation effects on structural materials on all HTM
System modelling to understand performance and operation constraints and select most promising options
Goals and milestones
Can molten salt mixtures, liquid metals or ceramic particles be used as efficient heat transfer media at T > 650° to achieve ηsys > 20% ?
51

## Slide 52: Subtopic 1 - Advanced Heat Transfer Media
10 kW Receiver and auxiliaries design, built and tested for all fluids
Evaluation of degradation effects on structural materials on all HTM
System modelling to understand performance and operation constraints and select most promising options
Design and Test of 100- 500 kW pilot scale installation
Goals and milestones
Can molten salt mixtures, liquid metals or ceramic particles be used as efficient heat transfer media at T > 650° to achieve ηsys > 20% ?
52

## Slide 53
SAM
Sun Photometer
53
Soiling and degradation characterization methods developed and installed at 10 different desert sites
Sunshape evaluation reference system developed
Impact of dust on high temperature ceramics characterized
Achievements in POF II
Accelerated aging procedures developed for aluminum reflectors
Subtopic 2 - Impact of Desert Environment
Is the concept fit to be operated for > 20 years in a desert environment?

## Slide 54: Subtopic 2 - Impact of Desert Environment
54
Influence of aerosols on optical plant performance with site specific sunshape and extinction data
Is the concept fit to be operated for > 20 years in a desert environment?
Goals and milestones

## Slide 55: Subtopic 2 - Impact of Desert Environment
55
Influence of aerosols on optical plant performance with site specific sunshape and extinction data
Quantification of soiling effects
Is the concept fit to be operated for > 20 years in a desert environment?
Goals and milestones

## Slide 56: Subtopic 2 - Impact of Desert Environment
56
Influence of aerosols on optical plant performance with site specific sunshape and extinction data
Quantification of soiling effects
Impact of dust on abrasion and corrosion of structural material
Is the concept fit to be operated for > 20 years in a desert environment?
Goals and milestones

## Slide 57: Subtopic 2 - Impact of Desert Environment
57
Influence of aerosols on optical plant performance with site specific sunshape and extinction data
Quantification of soiling effects
Impact of dust on abrasion and corrosion of structural material
Accelerated aging methods for structural outdoor materials (high temperature)
Is the concept fit to be operated for > 20 years in a desert environment?
Goals and milestones

## Slide 58: Subtopic 2 - Impact of Desert Environment
58
Influence of aerosols on optical plant performance with site specific sunshape and extinction data
Quantification of soiling effects
Impact of dust on abrasion and corrosion of structural material
Accelerated aging methods for structural outdoor materials (high temperature)
Simulation model for life time plant performance including soiling and degradation
Is the concept fit to be operated for > 20 years in a desert environment?
Goals and milestones

## Slide 59: Large scale facilities
Tower Research Facility Jülich
Solar Furnace
Solar Simulator
Liquid Metal Laboratory
Investment Proposal High Efficiency High Temperature Receiver System (HEHTRES)
≈ 500 kWth Pilot
59

## Slide 60: Cooperation
Sandia
Particle receiver development
Receiver simulation tools
Analysis of particle attrition
NREL
Atmospheric attenuation
Soiling on components
Modelling of mirror corrosion
CIEMAT
Meteorological analysis
Durability of key components
Programme TIS
Value of thermal storage to the grid system in different scenarios
Topic: Thermal Storage (SCI)
(Allied Partner, 16 FTE)
Molten salt composition and degradation
Liquid Metal storage integration
Particle Heat Exchanger
Topic: Methods for Material Development (EMR)
Corrosion and degradation of structural materials at high temperature
60

## Slide 61: Large scale facilities
Tower Research Facility Jülich
Solar Furnace
Solar Simulator
Liquid Metal Laboratory
Investment Proposal High Efficiency High Temperature Receiver System (HEHTRES)
≈ 500 kWth Pilot
61

## Slide 62: Conclusions
High risk/high reward research proposal to enable breakthrough technology that can achieve >20% annual system efficiency and efficient storage integration
Liquid metal competences and budget from Nuclear Safety Programme integrated
Synergies through allied partners from SCI Programme Topic “Thermal Storage”
  Materials competences integrated from EMR Topic “Methods and Concepts for Material Development”
  Leverage through international co-operation (CIEMAT, NREL, Sandia)
  Use of existing large scale facilities
Proof of concept planned in ≈500 kW scale as a basis for Tech-Transfer (HEHTRES - Investment Proposal)
62

## Slide 63: Vielen Dank für die Aufmerksamkeit Und hier noch ein Hinweis…..

## Slide 64: Mitglieder
Der Verband der Deutschen CSP umfasst aktuell 30 Mitgliedsunternehmen